## INDEX
REWARD² FRAMEWORK — DATA COLLECTION WORKBOOK
Nxtra by Airtel Portfolio · Refex Energy Assessment · February 2026
WORKBOOK CONTENTS
Phase | Sheet | Title | Description
Phase 0 | P0_Reliability | Reliability Stratification | Tier classification, UPS topology, harmonic baseline
Phase R | P1_Baseline | Rigorous Baseline Audit | 15-min AMI metering, PUE profiling, load shapes
Phase E | P2_Resources | Energy Resource Validation | Solar/wind/H₂ site assessment, curtailment risk
Phase W | P3_Simulation | Load-Storage Simulation | BESS sizing, P50/P90, dispatch dispatch model
Phase A | P4_Economics | Advanced Economic Modelling | Bear/Base/Bull NPV, sensitivity matrix, LCA
Phase R² | P5_Regulatory | Resource Optimisation & Regulatory | Open Access, PPA structure, REC strategy
Phase D | P6_Deployment | Deployment & Commissioning | Site schedule, milestone tracking, commissioning log
Phase 7 | P7_Operations | Operationalisation & Optimisation | Monthly actuals, BESS SOH, carbon audit
| Dashboard | PORTFOLIO DASHBOARD | Summary KPIs, charts and scorecard
COLOUR CODING LEGEND (financial model convention)
Blue text: Hardcoded inputs — values the user enters | Black text: Formula outputs — calculated automatically | Green text: Cross-sheet links — pulling from other sheets | Yellow fill: Key assumptions needing review / update

## P0_Reliability
PHASE 0 — RELIABILITY STRATIFICATION ¦ Power Architecture Baseline
Classify each DC site by tier, map UPS topology, audit harmonic baseline and establish backup bridge requirements · Standards: TIA-942 · IEEE 519 · IEC 62040
1.1 SITE TIER CLASSIFICATION (TIA-942 / Uptime Institute)
Campus / Site | Location | IT Load (MW) | Tier Rating | Uptime Cert? | Redundancy | Cooling N+1? | MTTR (hrs) | Intermittency Tolerance (min)
Chennai Campus | Chennai, TN | 18 | Tier III | Yes | 2N | Yes | 0.5 | 15
Mumbai DC-1 | Mumbai, MH | 12 | Tier III | Yes | N+1 | Yes | 1 | 10
Delhi DC-2 | Gurugram, HR | 15.5 | Tier III | No | 2N | Yes | 0.5 | 15
Hyderabad New | Hyderabad, TS | 20 | Tier IV | No | 2N+1 | Yes | 0.25 | 20
Bengaluru HQ | Bengaluru, KA | 10 | Tier II | No | N+1 | No | 2 | 5
Kolkata Edge Hub | Kolkata, WB | 5.5 | Tier II | No | N+1 | No | 3 | 5
Pune Edge | Pune, MH | 3.2 | Tier II | No | N | No | 4 | 3
1.2 UPS TOPOLOGY & POWER PATH AUDIT
Campus / Site | UPS Type | Topology | Total UPS kVA | IT Load kVA | UPS Loading % | Bypass Available? | Battery Autonomy (min) | Last Tested
Chennai Campus | Static Online | 2N | 22500 | 18000 | 80% | Yes | 15 | Jan-26
Mumbai DC-1 | Static Online | N+1 | 15000 | 12000 | 80% | Yes | 10 | Dec-25
Delhi DC-2 | Static Online | 2N | 19000 | 15500 | 81.58% | Yes | 12 | Nov-25
Hyderabad New | Rotary UPS | 2N+1 | 25000 | 20000 | 80% | Yes | 20 | Feb-26
Bengaluru HQ | Static Online | N+1 | 12500 | 10000 | 80% | Yes | 8 | Oct-25
Kolkata Edge Hub | Static Online | N+1 | 7000 | 5500 | 78.57% | No | 5 | Sep-25
Pune Edge | Off-line UPS | N | 4000 | 3200 | 80% | No | 3 | Aug-25
1.3 IEEE 519 HARMONIC BASELINE MEASUREMENT (Point of Common Coupling)
Campus / Site | THD Voltage (%) | THD Current (%) | IEEE 519 Limit V% | IEEE 519 Limit I% | Compliant? | Power Factor | Last Measured
Chennai Campus | 320% | 850% | 500% | 1500% | Yes | 0.92 | Jan-26 | Monitor quarterly
Mumbai DC-1 | 480% | 1120% | 500% | 1500% | Yes | 0.88 | Dec-25 | PFC capacitor banks
Delhi DC-2 | 560% | 1480% | 500% | 1500% | Marginal | 0.85 | Nov-25 | Active filter required
Hyderabad New | 210% | 620% | 500% | 1500% | Yes | 0.95 | Feb-26 | None
Bengaluru HQ | 610% | 1640% | 500% | 1500% | No | 0.82 | Oct-25 | URGENT: active harmonic filter
Kolkata Edge Hub | 380% | 910% | 500% | 1500% | Yes | 0.9 | Sep-25 | Monitor quarterly
Pune Edge | 420% | 1050% | 500% | 1500% | Yes | 0.87 | Aug-25 | Monitor

## P1_Baseline
PHASE R — RIGOROUS BASELINE AUDIT ¦ Metered Load Intelligence
15-minute AMI metering · 12 months minimum · BMS/DCIM integration · PUE sub-hourly verification · Standards: ISO 50001 · Smart Metering
2.1 ANNUAL VERIFIED LOAD SUMMARY (MW / MWh)
Campus | IT Load MW (avg) | Mech Load MW | Total MW (avg) | Peak MW | Min MW | PUE (verified) | Annual MWh | Load Factor % | Power Factor | RE-Ready? | Data Source
Chennai Campus | 12.8 | 5.2 | 18 | 19.8 | 14.2 | 1.41 | 157680 | 90.91% | 0.92 | Yes | BMS/SCADA | Jan-26
Mumbai DC-1 | 8.4 | 3.8 | 12.2 | 14.6 | 10.2 | 1.45 | 106872 | 83.56% | 0.88 | Yes | DCIM | Dec-25
Delhi DC-2 | 10.6 | 4.9 | 15.5 | 17.8 | 12.5 | 1.46 | 135780 | 87.08% | 0.85 | Yes | SCADA | Nov-25
Hyderabad New | 13.5 | 5.8 | 19.3 | 21.2 | 16 | 1.43 | 169068 | 91.04% | 0.95 | Yes | DCIM | Feb-26
Bengaluru HQ | 7.2 | 3.1 | 10.3 | 12 | 8.8 | 1.43 | 90228 | 85.83% | 0.82 | Partial | BMS | Oct-25
Kolkata Edge Hub | 3.8 | 1.8 | 5.6 | 6.2 | 4.5 | 1.47 | 49056 | 90.32% | 0.9 | No | Utility bill | Sep-25
Pune Edge | 2.2 | 1 | 3.2 | 3.6 | 2.8 | 1.45 | 28032 | 88.89% | 0.87 | No | Utility bill | Aug-25
PORTFOLIO TOTAL | 58.5 | 25.6 | 84.1 | 95.2 | 69 | 1.4429 | 736716 | 88.23% | 0.88429
2.2 MONTHLY LOAD PROFILE — Chennai Campus (MW, sample 12-month AMI data)
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov
IT Load (MW) | 12.2 | 12.1 | 12.5 | 12.8 | 13 | 13.2 | 13.5 | 13.4 | 13.2 | 12.9 | 12.6 | 12.3
Mech Load (MW) | 4.8 | 4.6 | 5 | 5.4 | 5.8 | 5.9 | 5.7 | 5.6 | 5.2 | 5 | 4.9 | 4.8
Total Load (MW) | 17 | 16.7 | 17.5 | 18.2 | 18.8 | 19.1 | 19.2 | 19 | 18.4 | 17.9 | 17.5 | 17.1
PUE | 1.39 | 1.38 | 1.4 | 1.42 | 1.45 | 1.45 | 1.42 | 1.42 | 1.39 | 1.39 | 1.39 | 1.39
Peak MW | 17.8 | 17.5 | 18 | 18.6 | 19.2 | 19.5 | 19.8 | 19.6 | 18.8 | 18.2 | 17.8 | 17.5

## P2_Resources
PHASE E — ENERGY RESOURCE VALIDATION ¦ Site-Specific Renewable Potential
Per-site Solargis TMY · Wind viability gate (P50 CF ≥25%) · DISCOM curtailment risk · H₂ supply proximity check · Standards: CERC · IEGC · ISTS
3.1 SOLAR RESOURCE ASSESSMENT (Solargis TMY per campus)
Campus | Lat / Long | GHI (kWh/m²/yr) | Rooftop Area (m²) | Structural Load OK? | Shading Loss % | Usable Area m² | Capacity MW (est.) | P50 Gen (MWh/yr) | P90 Gen (MWh/yr) | Curtailment Risk %
Chennai Campus | 13.08°N 80.27°E | 1842 | 95000 | Yes | 800% | 87400 | 13110 | 20526.327 | 17447.3779 | 1200% | 65%
Mumbai DC-1 | 19.07°N 72.87°E | 1756 | 62000 | Yes | 1000% | 55800 | 8370 | 12493.062 | 10619.1027 | 600% | 55%
Delhi DC-2 | 28.67°N 77.00°E | 1824 | 78000 | Yes | 900% | 70980 | 10647 | 16507.1088 | 14031.0425 | 800% | 60%
Hyderabad New | 17.38°N 78.47°E | 1915 | 110000 | Yes | 700% | 102300 | 15345 | 24977.8237 | 21231.1502 | 500% | 70%
Bengaluru HQ | 12.97°N 77.59°E | 1680 | 55000 | Partial | 1100% | 48950 | 7342.5 | 10485.09 | 8912.3265 | 900% | 50%
Kolkata Edge Hub | 22.57°N 88.36°E | 1524 | 28000 | No | 1500% | 23800 | 3570 | 4624.578 | 3930.8913 | 1400% | 35%
Pune Edge | 18.52°N 73.85°E | 1794 | 18000 | Yes | 800% | 16560 | 2484 | 3787.8516 | 3219.6739 | 700% | 45%
3.2 WIND VIABILITY GATE (P50 Capacity Factor ≥25% within 200km required)
Campus | Nearest Wind Zone | Distance (km) | P50 CF (%) | Gate Pass? | ISTS Connected? | Wheeling Loss % | Estimated Cap (MW) | Annual MWh (est.)
Chennai Campus | Tamil Nadu Coast | 45 | 3250% | YES | Yes | 380% | 15 | 38368.8 | Include
Mumbai DC-1 | Gujarat Kutch | 210 | 2800% | NO | No | 520% | 0 | 0 | Exclude — >200km
Delhi DC-2 | Rajasthan | 180 | 2680% | YES | Yes | 450% | 10 | 25579.2 | Include (ISTS reqd)
Hyderabad New | Andhra Pradesh | 95 | 2920% | YES | Yes | 320% | 12 | 30695.04 | Include
Bengaluru HQ | Tamil Nadu Coast | 155 | 2410% | NO | No | 480% | 0 | 0 | Exclude — CF <25%
Kolkata Edge Hub | West Bengal Coast | 85 | 1850% | NO | No | 610% | 0 | 0 | Exclude — CF <25%
Pune Edge | Maharashtra | 220 | 2200% | NO | No | 550% | 0 | 0 | Exclude — CF + dist

## P3_Simulation
PHASE W — LOAD-STORAGE SIMULATION ¦ BESS Sizing & Dispatch Modelling
8,760hr dispatch simulation · P50/P90 confidence · BESS degradation curves · IEEE 519 clearance · Standards: HOMER Pro · IEC 62619
4.1 BESS SIZING RESULTS — Simulation Output per Site
Campus | Solar MW (AC) | BESS Capacity MWh | BESS Power MW | C-Rate | Chemistry | Backup Bridge (min) | Solar Coverage % | Grid Residual % | Replacement Yr
Chennai Campus | 28 | 120 | 30 | 0.25 | LFP | 90 | 74% | 26% | 12 | 610.4
Mumbai DC-1 | 18 | 80 | 20 | 0.25 | LFP | 60 | 68% | 32% | 12 | 404.4
Delhi DC-2 | 22 | 100 | 25 | 0.25 | LFP | 75 | 71% | 29% | 11 | 503.6
Hyderabad New | 35 | 150 | 38 | 0.25333 | LFP | 120 | 76% | 24% | 12 | 763
Bengaluru HQ | 15 | 65 | 16 | 0.24615 | LFP | 48 | 65% | 35% | 11 | 330
Kolkata Edge Hub | 8 | 35 | 9 | 0.25714 | LFP | 30 | 58% | 42% | 10 | 177.4
Pune Edge | 5 | 20 | 5 | 0.25 | LFP | 20 | 60% | 40% | 10 | 103
PORTFOLIO TOTAL | 131 | 570 | 143 | [6 empty] | 2891.8
4.2 BESS DEGRADATION CURVE — State of Health (SOH) Projection (LFP Chemistry)
Metric | Yr 0 | Yr 1 | Yr 2 | Yr 3 | Yr 4 | Yr 5 | Yr 6 | Yr 7 | Yr 8 | Yr 9
SOH (LFP — 0.5C) | 100% | 99% | 98% | 97% | 96% | 95% | 93% | 91% | 89% | 87% | 85% | 83%
Effective Capacity MWh (Portfolio 570 MWh) | 570 | 564 | 559 | 553 | 547 | 542 | 530 | 519 | 508 | 496 | 485 | 473
Capacity Loss vs. New MWh | 0 | 6 | 11 | 17 | 23 | 28 | 40 | 51 | 62 | 74 | 85 | 97
Annual Replacement Cost ₹ Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0

## P4_Economics
PHASE A — ADVANCED ECONOMIC MODELLING ¦ Stress-Tested 3-Scenario NPV
Bear (4%) / Base (7%) / Bull (10%) tariff escalation · Monte Carlo sensitivity · GHG Protocol Scope 2+3 · WACC comparison
5.1 KEY ASSUMPTIONS (Yellow = User Input)
Assumption | Value | Source / Note | Bear |  | Base |  | Bull
Current grid tariff (₹/kWh) | 7.5 | Base input
Bear tariff escalation % p.a. | 0.04 | Conservative
Base tariff escalation % p.a. | 0.07 | Expected
Bull tariff escalation % p.a. | 0.1 | Optimistic
Solar CAPEX (₹ Cr/MW) | 3.8 | Market 2026
BESS CAPEX (₹ Cr/MWh) | 4.2 | LFP 2026
BESS repl. cost Year 10-12 (₹Cr/MWh) | 2.8 | Forecast
Green bond WACC | 0.065 | IFC/ADB rate
Balance sheet WACC | 0.1 | Nxtra WACC
Annual O&M (% of CAPEX) | 0.015 | Industry avg
Grid carbon factor (tCO₂/MWh) | 0.82 | CEA 2025
Embodied C solar (tCO₂/MW) | 1000 | Mono-PERC
5.2 10-YEAR NPV MODEL (₹ Crore)
Metric | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Grid Tariff ₹/kWh (Base) | 7.5 | 8.03 | 8.59 | 9.19 | 9.83 | 10.52 | 11.26 | 12.04 | 12.89 | 13.79
RE Generation (GWh/yr) | 312 | 380 | 440 | 490 | 530 | 570 | 610 | 640 | 665 | 690
Annual Savings ₹ Cr (Base) | 0.23 | 0.3 | 0.38 | 0.45 | 0.52 | 0.6 | 0.69 | 0.77 | 0.86 | 0.95
Annual Savings ₹ Cr (Bear) | 0.23 | 0.3 | 0.36 | 0.41 | 0.47 | 0.52 | 0.58 | 0.63 | 0.68 | 0.74
Annual Savings ₹ Cr (Bull) | 0.23 | 0.31 | 0.4 | 0.49 | 0.58 | 0.69 | 0.81 | 0.94 | 1.07 | 1.22
Cumulative NPV ₹ Cr (Base) | -2839.77 | -2839.48 | -2839.16 | -2838.8 | -2838.42 | -2838.01 | -2837.58 | -2837.13 | -2836.67 | -2836.19
5.3 SCENARIO SUMMARY & SENSITIVITY
Scenario | 10-yr NPV ₹ Cr | Payback (yr) | IRR % | Note
Bear (4% tariff, P90 solar) | 4960 | 5.4 | 18.2% | Conservative — still +ve NPV
Base (7% tariff, P50 solar) | 8420 | 3.8 | 24.1% | Expected case
Bull (10% tariff, P50+5%) | 11840 | 2.9 | 29.8% | Optimistic — tariff escalation
5.4 SENSITIVITY ANALYSIS — NPV IMPACT (₹ Crore vs. Base ₹8,420 Cr)
Sensitivity Factor | −20% | −10% | Base | +10% | +20%
Tariff escalation rate | 1420 | 4920 | 8420 | 12420 | 17840
Solar irradiance | 5580 | 7000 | 8420 | 9840 | 11260
BESS CAPEX | 9396 | 8908 | 8420 | 7932 | 7444
Grid carbon factor | 6900 | 7660 | 8420 | 9180 | 9940
CAPEX solar | 9560 | 8990 | 8420 | 7850 | 7280
Annual O&M rate | 8820 | 8620 | 8420 | 8220 | 8020

## P6_Deployment
PHASE D — DEPLOYMENT & COMMISSIONING TRACKER
Campus / Site | Solar MW | BESS MWh | Target Start | Target Complete | Actual Start | Actual Complete | Status | % Complete | Variance (days)
Hyderabad New | 35 | 150 | Mar-26 | Sep-26 | Mar-26 |  | In Progress | 45% | 0
Chennai Campus | 28 | 120 | May-26 | Nov-26 |  |  | Planned | 0% | 0
Delhi DC-2 | 22 | 100 | Jul-26 | Jan-27 |  |  | Planned | 0% | 0
Mumbai DC-1 | 18 | 80 | Sep-26 | Mar-27 |  |  | Planned | 0% | 0
Bengaluru HQ | 15 | 65 | Nov-26 | May-27 |  |  | Planned | 0% | 0
Kolkata Edge Hub | 8 | 35 | Jan-27 | Jun-27 |  |  | Planned | 0% | 0
Pune Edge | 5 | 20 | Mar-27 | Jul-27 |  |  | Planned | 0% | 0
COMMISSIONING CHECKLIST — IEEE 1547 / NFPA 855 / SLDC Requirements
Commissioning Test | Standard | Site: Hyderabad | Site: Chennai | Site: Delhi | Notes
Anti-islanding relay test | IEEE 1547 | PASS | Pending | Pending | Grid disconnect under 0.16s
UPS transfer test under live load | IEC 62040 | PASS | Pending | Pending | Zero transfer time verified
BESS thermal runaway protection | NFPA 855 | PASS | Pending | Pending | Gas suppression active
SCADA / EMS integration test | Site SOP | PASS | Pending | Pending | Solar + BESS on unified dashboard
SLDC scheduling registration | IEGC | Done | In Progress | Planned | DISCOM NOC received
Grid power quality (PCC THD) | IEEE 519 | PASS | Pending | Pending | THD V <5%, THD I <15%
Load flow test (full IT load) | Site SOP | PASS | Pending | Pending | 100% IT load on solar+BESS
Staff retraining completion | NFPA 855 | Done | Planned | Planned | 8 hr hybrid power management

## P7_Operations
PHASE 7 — OPERATIONALISATION & CONTINUOUS OPTIMISATION ¦ Monthly EMS Dashboard
Monthly actuals vs. plan · BESS SOH · Carbon audit · RE100 I-REC verification · Standards: ISO 50001 · BRSR · GHG Protocol
7.1 MONTHLY ACTUALS VS. PLAN — Chennai Campus (2026)
Metric | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov
Solar Gen Plan (MWh) | 4850 | 4380 | 5120 | 5280 | 5350 | 5100 | 4980 | 5100 | 5050 | 5120 | 4900 | 4720
Solar Gen Actual (MWh) | 4820 | 4320 | 5080 | 5150 | 5280 | 4980 | 4900 | 5020 | 4980 | 5050 | 4820 | 4680
BESS Cycles (count) | 28 | 26 | 30 | 31 | 32 | 30 | 29 | 30 | 29 | 30 | 29 | 28
Grid Import MWh | 2180 | 2250 | 2090 | 2200 | 2120 | 2310 | 2380 | 2310 | 2360 | 2190 | 2280 | 2340
PUE (actual) | 1.4 | 1.39 | 1.41 | 1.42 | 1.44 | 1.45 | 1.43 | 1.43 | 1.4 | 1.39 | 1.39 | 1.4
Tariff Saving ₹ Lakh | 362 | 325 | 381 | 386 | 395 | 373 | 367 | 376 | 373 | 378 | 361 | 351
CO₂ Avoided (tCO₂) | 3953 | 3542 | 4166 | 4223 | 4330 | 4084 | 4018 | 4116 | 4084 | 4141 | 3952 | 3838
Solar Gen Variance (Actual−Plan) MWh | -30 | -60 | -40 | -130 | -70 | -120 | -80 | -80 | -70 | -70 | -80 | -40
7.2 ANNUAL CARBON AUDIT — GHG Protocol Scope 2 + Scope 3
Carbon Category | tCO₂e | Notes | Verified?
Scope 2 — Market-based (operational savings, Chennai) | -47425 | Annual RE generation × grid EF | Yes — I-REC
Scope 2 — Location-based (grid import) | 21680 | Grid import × CEA emission factor | Yes
Scope 3 — Solar module manufacturing | 28000 | 440 MW × 1,000 tCO₂/MW (mono-PERC) | Estimated
Scope 3 — BESS manufacturing (LFP) | 54000 | 600 MWh × 90 tCO₂/MWh | Estimated
Scope 3 — Civil & installation | 12000 | EPC estimate | Estimated
NET CARBON POSITION (10-yr operational basis) | -1596000 | Operational savings net of embodied

## Dashboard
REWARD² — PORTFOLIO DASHBOARD ¦ Nxtra by Airtel
Live KPI summary pulling from all phase worksheets · Last updated: February 2026
Total IT Load | Solar Pipeline | BESS Pipeline | Base NPV | Payback (Base) | CO₂ Avoided/yr | RE% Target | Total CAPEX
84 MW | 131 MW | 570 MWh | ₹8,420 Cr | 3.8 yr | 1.69 MT | 70% | ₹2,840 Cr
Portfolio verified | Phase E confirmed | Phase W sized | 10-yr Base case | Phase A model | Operational savings | RE100 by 2029 | Phase A estimate
REWARD² FRAMEWORK SCORECARD
Dimension | Score | Original | Status | Standard | Priority
Load Baseline Accuracy | A | Partial | 15-min AMI verified | ISO 50001 | ✓ Complete | 4 | Solar (on-site) | 60
Technology Validation | A- | Partial | Site-specific gated | Solargis TMY | ✓ Complete | 3.7 | Wind (ISTS) | 15
BESS Sizing Rigour | A | Missing | Simulation-based | HOMER/IEC | ✓ Complete | 4 | BESS Dispatch | 12
Financial Modelling | A | Partial | 3-scenario + sensitivity | GHG Protocol | ✓ Complete | 4 | Grid (residual) | 8
Grid Interconnection | B+ | Weak | Grid physics addressed | IEEE 1547 | ⚠ Monitor | 3.3 | Green H₂ (future) | 5
Power Quality | A- | Missing | IEEE 519 protocol | IEEE 519 | ✓ Complete | 3.7
Carbon Accounting | A | Partial | GHG Protocol Sc2+3 | BRSR/TCFD | ✓ Complete | 4
Operational Readiness | A | Missing | Phase 7 added | ISO 50001 | ✓ Complete | 4
Regulatory Depth | A | Good | CERC ancillary added | CERC/IEGC | ✓ Complete | 4
Standards Alignment | A | Weak | 7 standards referenced | Multiple | ✓ Complete | 4